## Summary
Key | Value
App | OTScan 2.0.1
Nmap Version (XML) | 7.95
Nmap Args (XML) | nmap -sT -sV 192.168.10.0/24
Hosts (count) | 5
Ports (count) | 8
Ports open (count) | 8
Ampel-Status (SEC-BP) | RED
SEC-BP-krit. Ports offen | 8
Top Vendors | Siemens(1), Telemecanique Electrique(1), RuggedCom(1), Bosch Rexroth(1), UNKNOWN(1)
Top Open Ports | 502/tcp(2), 102/tcp(1), 80/tcp(1), 4840/tcp(1), 21/tcp(1), 23/tcp(1), 47808/udp(1)
Top Critical Open Ports (SEC-BP) | 502/tcp(2), 102/tcp(1), 80/tcp(1), 4840/tcp(1), 21/tcp(1), 23/tcp(1), 47808/udp(1)

## Hosts
IP Adresse | MAC Adresse | Hersteller | Geraeteklasse | Status | Status Reason | Critical Open Ports | Firewall-Status | OS (bester Treffer) | OS (Accuracy) | OS Typ (OSClass) | OS Vendor | OS Family | OS Gen | OS Matches (alle) | Nmap Hostnames | Service-Hostname | SNMP Hostname | Workgroup | S7 System Name | S7 Module | S7 Version | BACnet | Offene TCP-Ports | Offene UDP-Ports | UDP open¦filtered Ports | Services (Detail) | Scripts/Output | Distance | Uptime (s) | Lastboot | Extra
192.168.10.11 | 00:1B:1B:11:22:33 | Siemens | SPS/PLC (Siemens S7) | up | arp-response | 102/tcp(S7comm/ISO-TSAP (Siemens S7)), 80/tcp(HTTP) |  | Siemens SIMATIC S7-1200 | 95 | PLC | Siemens | embedded |  | Siemens SIMATIC S7-1200 | plc-presse-3.werk.local |  |  |  | SIMATIC 1200 | 6ES7 214-1AG40-0XB0 | 4.2.3 |  | 102,80 |  |  | 102/tcp (iso-tsap) - Siemens S7 PLC; 80/tcp (http) - Siemens S7-1200 httpd | [s7-info]: Module: 6ES7 214-1AG40-0XB0 / Basic Hardware: 6ES7 214-1AG40-0XB0 / Version: 4.2.3 / System Name: SIMATIC 1200 / Serial Number: S C-X4U421302016 / Plant Identification: Halle-3 Presse
192.168.10.21 | 00:80:F4:44:55:66 | Telemecanique Electrique | OPC-UA-Server (SCADA/DCS) | up | arp-response | 21/tcp(FTP), 23/tcp(Telnet), 4840/tcp(OPC UA (Binary)), 502/tcp(Modbus/TCP) | [8 empty] | m241-Pumpe_Ölkühlung | [7 empty] | 502,4840,21,23 |  |  | 502/tcp (modbus) - Modbus TCP; 4840/tcp (opcua-tcp) - OPC UA; 21/tcp (ftp) - vsftpd; 23/tcp (telnet) | [modbus-discover]: sid 0x1: / Slave ID data: Schneider Electric M241 ¦ [opc-ua-info]: SecurityPolicy: None / ApplicationName: Modicon M241
192.168.10.60 | 00:0A:DC:77:88:99 | RuggedCom | Gebäudeautomation (BACnet) | up | arp-response | 47808/udp(BACnet/IP) | [17 empty] | 47808 |  | 47808/udp (bacnet) - BACnet | [bacnet-info]: Vendor ID: Siemens (7) / Firmware: 11.2
192.168.10.34 | 00:12:4B:AA:BB:CC | Bosch Rexroth | SPS/PLC (Bosch Rexroth IndraControl/ctrlX) | up | arp-response | 502/tcp(Modbus/TCP) | [16 empty] | 502 |  |  | 502/tcp (modbus) - Janitza UMG 96-RM
192.168.10.99 | 00:11:22:33:44:55 |  |  | up | arp-response

## Ports
ip | protocol | port | state | reason | service_name | product | version | extrainfo | cpe | Is Critical | Critical Label | Kategorie | Quelle
192.168.10.11 | tcp | 102 | open | syn-ack | iso-tsap | Siemens S7 PLC |  |  |  | 1 | S7comm/ISO-TSAP (Siemens S7) | OT | IANA, CISA, NIST800-82
192.168.10.11 | tcp | 80 | open | syn-ack | http | Siemens S7-1200 httpd |  |  |  | 1 | HTTP | IT | SEC-BP
192.168.10.21 | tcp | 502 | open | syn-ack | modbus | Modbus TCP |  |  |  | 1 | Modbus/TCP | OT | IANA, CISA, NIST800-82
192.168.10.21 | tcp | 4840 | open | syn-ack | opcua-tcp | OPC UA |  |  |  | 1 | OPC UA (Binary) | OT | IANA, IEC62443
192.168.10.21 | tcp | 21 | open | syn-ack | ftp | vsftpd |  |  |  | 1 | FTP | IT | SEC-BP
192.168.10.21 | tcp | 23 | open | syn-ack | telnet |  |  |  |  | 1 | Telnet | IT | SEC-BP
192.168.10.60 | udp | 47808 | open | syn-ack | bacnet | BACnet |  |  |  | 1 | BACnet/IP | OT | IANA, ITI-PORTS
192.168.10.34 | tcp | 502 | open | syn-ack | modbus | Janitza UMG 96-RM |  |  |  | 1 | Modbus/TCP | OT | IANA, CISA, NIST800-82

## Scripts
ip | script_id | output
192.168.10.11 | s7-info | Module: 6ES7 214-1AG40-0XB0 Basic Hardware: 6ES7 214-1AG40-0XB0 Version: 4.2.3 System Name: SIMATIC 1200 Serial Number: S C-X4U421302016 Plant Identification: Halle-3 Presse
192.168.10.21 | modbus-discover | sid 0x1: Slave ID data: Schneider Electric M241
192.168.10.21 | opc-ua-info | SecurityPolicy: None ApplicationName: Modicon M241
192.168.10.60 | bacnet-info | Vendor ID: Siemens (7) Firmware: 11.2